## identified_leaks
_record_id | _title | _version | _server_created_at | _server_updated_at | _created_at | _project | _created_by | _updated_by | _geometry | _latitude | _longitude | date | leak_address | leak_address_locality | zone | leak_asset_type | asset_id | locationid | flow_rate_lmin | leak_location | has_the_leak_been_called_in_by_ds_technician | job_ref | distance_from_paint_mark | leak_visible | comments | photo | significant_leak_video_capture | reported_to_client
f0e5e20c-6095-4b51-b0ac-ae1165fcd951 | 17 Cook Street McCrae Victoria 3938 Australia | 2 | 2025-06-06 03:45:09 UTC | 2025-06-07 08:34:52 UTC | 2025-06-06 03:17:07 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.93667410662763 -38.35954250455144) | -38.3595 | 144.9367 | 2025-06-06 | 17 Cook Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Customer Leak |  |  | 20 |  | no | LD024 |  | no | Turned meter on & it started spinning over. Walked up very steep long driveway & noticed water running down steep slope near top of driveway. Walked around to corner footing of house & noticed water pushing through ground at stone footing of building. Near where telstra cable enters building. Couldn't probe onto service line. Hard ground. Suspect that leak may be on service outside building or inside behind stone footing. 1200/hr Turned meter off as requested | c715b512-36b9-428d-904d-31317881f297, 5a4db635-000a-4af1-b504-b1f878301a9f, 16c64666-bc57-4d20-b4f7-9c1ba05ab241, b1e842e2-f795-4985-9c7f-dd93a59c9f28, 361eecee-9173-4ce5-8bbf-926ab48fc4a2, a617213e-476c-4abd-93a7-5d1be849249f |  | no
d487ec78-08af-420b-a690-65053c424638 | 93 Flinders Street McCrae Victoria 3938 Australia | 2 | 2025-06-06 02:34:24 UTC | 2025-06-06 03:21:23 UTC | 2025-06-06 02:16:13 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.92910586737574 -38.35880053102263) | -38.3588 | 144.9291 | 2025-06-06 | 93 Flinders Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Toilet Cistern |  |  | 8 |  | no | LD023 |  | no | Arrived onsite. Builder onsite. Found meter turned off. Turned meter on & it started spinning over. Sounded 3x garden taps in front yard, all with distant faint noise. Meanwhile Builder used toilet & noticed cistern continuously flowing, he fixed cistern & flow stopped, resounded meter & noise stopped & usage stopped. Cistern was stuck open MSR-29112 | af913430-8fc7-4a90-a326-d98339aba7bf |  | no
19c517e4-076c-44a1-9fae-89c96452e0f5 | 29 Navigator Street McCrae Victoria 3938 Australia | 2 | 2025-06-04 02:45:13 UTC | 2025-06-05 23:17:36 UTC | 2025-06-04 02:39:47 UTC | Service Stream | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.9350722 -38.3551544) | -38.3552 | 144.9351 | 2025-06-04 | 29 Navigator Street McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Meter |  |  | 0.5 |  | no |  |  | no | Possible fault meter. Picked up noise on meter, louder on customer side. Meter not moving. Shut off meter & noise stopped. Suggest replacing meter & sounding for customer leaks | f799457e-3ecf-4de6-a81a-733750cff9db, c3579ba7-7de4-4a8b-94b2-223ca1313c63 |  | yes
2d0e8830-8cb5-4363-bed2-3c60c4e7a726 | 14 Poole Street McCrae Victoria 3938 Australia | 2 | 2025-06-04 02:50:45 UTC | 2025-06-05 23:17:35 UTC | 2025-06-04 02:46:45 UTC | Service Stream | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.935554 -38.3546601) | -38.3547 | 144.9356 | 2025-06-04 | 14 Poole Street McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | customer leak & meter tap |  |  | 1 |  | no |  |  | yes | Leak on sprinkler head next to driveway. Water running down driveway. Cannot shut off Meter. Recommend replacing meter tap & notifying customer of leak on sprinkler system | 2af3f618-c952-4746-997b-cfe369db13e9, 68d8e20b-ff82-4c25-bc32-7fe0926e65cf, c6055614-e7ee-4315-b022-fcab4ef84d5f |  | yes
3b6b2a04-98fb-4101-8ee6-e84e155d430c | Unit 3, 48 Armstrong Road McCrae Victoria 3938 Australia | 3 | 2025-06-04 03:53:26 UTC | 2025-06-04 04:05:25 UTC | 2025-06-04 03:45:16 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.9194161 -38.3638759) | -38.3639 | 144.9194 | 2025-06-04 | Unit 3, 48 Armstrong Road McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Customer Leak |  |  | 0.3 |  | no | LD022 |  | no | Arrived onsite, no one home. Meter spinning around, sounded garden tap at front of unit 3, no noise. Called Graham. Graham Arrived gained access to rear of property, sounded rear garden tap, picked up small noise. Tightened tap & noise stopped. Sounded fittings up sideway..no other noises. Checked meter again & meter stopped spinning...no noise. Informed Graham of my findings & that rear garden tap may have been used & not turned off fully/left on/dribbling for a long period of time . | bf02b4de-5cb2-4255-8822-a19184846ab0 |  | no
5089b9dc-8f85-40f0-8d40-6279986d2f85 | Bayview Rd McCrae VIC 3938 AU | 2 | 2025-06-04 03:12:57 UTC | 2025-06-04 03:13:56 UTC | 2025-06-03 00:46:04 UTC | Service Stream | Scott Grace | Scott Grace | SRID=4326;POINT(144.93956889970687 -38.34894612900759) | -38.3489 | 144.9396 | 2025-06-03 | Bayview Rd McCrae VIC 3938 AU | McCrae | South East Water, Reactive Leaks | Tracing |  |  | 0.1 |  | no | 1347304/001 |  | no | Met surveyor/SEW on-site to attempt to trace metallic and PVC pipelines. Successfully traced metallic pipeline which crossed Bayview Road and run down near the Fence-line to valves/hydrants. Struggled to pick up the PVC pipeline using the AML tool. Would require Vac truck to prove what was being picked up with the AML tool. Another option to trace the PV pipeline would be to use GPR, dependent on soil type, depth of main etc. | 033c84cd-3df2-4674-90fc-c22009bc6626, 09dc7f79-98bd-4a35-9512-3e201bf5e770, 0af52470-4c42-426d-89bf-e8fd9aac83c8, 8537c690-7ccc-4d65-94a7-a9d715e3e2b3 |  | no
bd55ab48-c6a2-496d-9e9d-a63234ca3023 | 56 Cairn Road McCrae Victoria 3938 Australia | 2 | 2025-06-03 02:26:50 UTC | 2025-06-04 00:24:12 UTC | 2025-06-03 02:25:27 UTC | Service Stream | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.9298545 -38.3629943) | -38.363 | 144.9299 | 2025-06-03 | 56 Cairn Road McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Hydrant |  |  | 0.5 |  | no |  |  | no | Ground hydrant leaking from ball | f76b0e5c-d377-41de-9fe7-1aaef68579f7, 734f5355-ea31-40e6-8b5a-a233219802dc |  | yes
4633a1d3-cd4b-49e8-8074-6a00a8786733 | 47 Somers Avenue McCrae Victoria 3938 Australia | 2 | 2025-06-03 02:49:42 UTC | 2025-06-04 00:24:11 UTC | 2025-06-03 02:47:26 UTC | Service Stream | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93003213016948 -38.361160909709994) | -38.3612 | 144.93 | 2025-06-03 | 47 Somers Avenue McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Valve |  |  | 5 |  | no |  |  | yes | Valve leak. Corner Cairns Av. Water running downhill Into property | 3eb5f6a5-3896-4157-ac00-f6f755ff9982, d3dbfcfe-4b5e-4049-bffc-e646dbe54c10 |  | yes
aac222b9-bd41-4d60-a26a-9069a31ea8d0 | 37 Somers Avenue McCrae Victoria 3938 Australia | 2 | 2025-06-03 04:15:40 UTC | 2025-06-04 00:24:10 UTC | 2025-06-03 04:13:35 UTC | Service Stream | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93140156737576 -38.360846235108475) | -38.3608 | 144.9314 | 2025-06-03 | 37 Somers Avenue McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Hydrant |  |  | 0.3 |  | no |  |  | no | Ground hydrant leaking from ball | 8acef34b-cde2-4033-88e9-6ab3ac83b7ce, ccb967fa-fa21-4718-be7b-5a5e07624568 |  | yes
32860f8f-2b75-45b3-ba09-edb61c91e22c | 77 Flinders Street McCrae Victoria 3938 Australia | 3 | 2025-05-15 00:05:26 UTC | 2025-05-30 02:48:33 UTC | 2025-05-14 23:58:31 UTC | Downer | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.9311911 -38.3571778) | -38.3572 | 144.9312 | 2025-05-15 | 77 Flinders Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | No Leaks Found |  |  | 0 |  | no | 1343726/001 |  | no | Re-attended job at the request of Downer. Resounded meter & surrounds..dead quiet Gas line appears to be in line with water meter...potentially picking up noise from gas line if the customer has something running at night? Another option would be to replace the meter in case the current meter installed is faulty. | 104eeb3f-b6b2-4303-8e8d-ddaba128593f, 337cdbff-2e01-490f-b97d-c074e5115b63, 9dc2d7fa-2076-464e-b40a-b7f8beaab0e0 |  | no
885143bd-0b06-44e0-a468-a9f05e6db183 | Unit 2, 6 Bentley Road McCrae Victoria 3938 Australia | 3 | 2025-05-28 22:01:12 UTC | 2025-05-29 02:47:28 UTC | 2025-05-28 21:54:47 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.92045223835203 -38.36252195189251) | -38.3625 | 144.9205 | 2025-05-29 | Unit 2, 6 Bentley Road McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | No Leaks Found |  |  | 0 |  | no | LD0021 |  | no | Sounded meter in driveway and no leak noise was detected or movement on meter. | d2dd2b36-1145-4184-bd78-1849a6ad1fa2, c7dbe3b0-1f01-400c-b95c-9f6aaab936a4 |  | no
a742e150-ac92-4b9c-b329-aebd7711e722 | 589 Point Nepean Road McCrae Victoria 3938 Australia | 2 | 2025-05-28 22:30:23 UTC | 2025-05-29 02:42:42 UTC | 2025-05-28 22:25:48 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.9363341 -38.3451248) | -38.3451 | 144.9363 | 2025-05-29 | 589 Point Nepean Road McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | No Leaks Found |  |  | 0 |  | no | LD0020 |  | no | No leaks. Sounded meter, heard ticking sound from tap timer, disconnected timer & no leak noises picked up . No movement on meter. Found meter tap in "on" position. Issue potentially has been resolved or could be a faulty meter. MSR-290170 | dcb71951-2523-42f0-b4d3-dd5a588803cc, 6d46a731-bb3e-4ebb-ac01-e79663551e5c |  | no
50993e3f-de04-4513-a27c-dce69343ce14 | 13 Bentley Road McCrae Victoria 3938 Australia | 3 | 2025-05-26 03:10:53 UTC | 2025-05-26 06:40:03 UTC | 2025-05-26 03:02:04 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.9199253 -38.363333) | -38.3633 | 144.9199 | 2025-05-26 | 13 Bentley Road McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Customer Leak |  |  | 0.1 |  | no | LD00018 |  | no | Arrived onsite, plumbers already onsite & have replaced sections of service line down the side of house. They dug around front garden tap thinking there was a weeping leak around garden tap Junction, but ground dry. They will replace garden tap as riser is rusting away. Turned meter back on & no noise or movement on meter. Believe issue has already been resolved by replacing sections of service down the sideway 2hrs travel 1hr onsite | 9cf65606-b923-4948-9aed-c3ac231a7400, e045e760-d9ae-489d-b560-c074b8b56a2d |  | no
c43924ea-f1d0-42d7-b963-276c1f8bd1a1 | 2 Prospect Hill Road McCrae Victoria 3938 Australia | 4 | 2025-05-14 04:24:06 UTC | 2025-05-14 06:28:23 UTC | 2025-05-14 04:20:43 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.9375614 -38.346596) | -38.3466 | 144.9376 | 2025-05-14 | 2 Prospect Hill Road McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | No Leaks Found |  |  | 0 |  | no | LD0016 |  | no | Arrive onsite to investigate a potential leak at the request of Service Stream. Sounded meter and no movement on meter or leak noise picked up, sounded surrounding assets no noises picked up either. No wet patches or water anywhere. No leaks found. Works nearby on the main at Cornell/Browne/Coburn. | 10adb041-3a8f-4534-8994-868a6a4194c4, a96a00c9-2406-411d-9096-b13842f796f2 |  | no
78c6bfb3-d49c-4aa2-9ecd-7c08d5a23414 | 21 Browne Street McCrae Victoria 3938 Australia | 2 | 2025-05-14 03:48:33 UTC | 2025-05-14 03:52:07 UTC | 2025-05-14 03:39:59 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.9347833 -38.3486975) | -38.3487 | 144.9348 | 2025-05-14 | 21 Browne Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | No Leaks Found |  |  | 0 |  | no | LD0015 |  | no | No leaks found. No movement on meter. Turned garden tap on & off. Pressure seems normal Possibly air trapped inside customer pipework after installing new meter causing issues. Air may need to be flushed out of pipes. House is halfway down dead end main & they are working on the water at the top of the street. | c05c9e33-e3c6-4631-8227-1bdf0c98c3d9 |  | no
fa8b3e45-c1b3-418f-b366-261f0cf10a23 | 77 Flinders Street McCrae Victoria 3938 Australia | 2 | 2025-05-14 03:26:25 UTC | 2025-05-14 03:28:51 UTC | 2025-05-14 03:10:26 UTC | Downer | Stuart Haggett | Stuart Haggett | SRID=4326;POINT(144.9302618 -38.3575952) | -38.3576 | 144.9303 | 2025-05-14 | 77 Flinders Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | No Leaks Found |  |  | 0 |  | no | 1343726/001 |  | no | Not convinced there is a leak here. Sounded meter....dead quiet,...apart from. Distant noise from nearby prv/zone valve/strainer (WB131) Ran straight line Correlation which peaked on zone valve Surveyed yesterday afternoon 13/5 & early this morning 14/5 Yesterday noticed good noise on meter. Shut of meter & noise stopped, turned on meter & noise started again. Today meter is dead quiet...apart from distant noise on zone valve/strainer (WB131) | f0c84e89-6dbc-4e0a-ba9c-6a4ea5db8817, 611e3bba-4645-4cf4-8d09-50126b7373af, 073558d0-ddf4-4bff-8f24-5269a1f6d922 |  | no
6c6d16f3-a2e0-480b-ab68-bcb86ec14842 | 711 Point Nepean Road McCrae Victoria 3938 Australia | 2 | 2025-05-09 07:02:51 UTC | 2025-05-14 03:08:38 UTC | 2025-05-09 05:11:54 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.925306 -38.34986) | -38.3499 | 144.9253 | 2025-05-09 | 711 Point Nepean Road McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Customer Leak |  |  | 0.8 |  | no | LD0013 |  | no | 0.8l/m (50l/h) Sounded outside taps, back tap dead quiet, front tap slight noise Service stream arrived, dug a few holes both sides of front garage & in Front garden, with no luck, although I am picking up noise in pot holes. Discovered that service is pvc Sounded with ground phone across garage slab & also picking up noise across garage floor, one half of concrete slab slightly louder. Service stream will install some stop taps both sides of garage to narrow leak down at a future date. & if leak is under concrete slab they may re-route service line 2 hr onsite | dab83aa1-28ce-49a3-b52e-0f9ac2a9039f, 92c59259-f727-4113-abe1-396dbf4f907f |  | no
6b53cdab-c6b3-4d69-9448-296fe159ab88 | 17 Charles Street McCrae Victoria 3938 Australia | 3 | 2025-05-06 23:52:12 UTC | 2025-05-14 03:08:09 UTC | 2025-05-06 23:37:39 UTC | Service Stream | Morgan Williams | Scott Grace | SRID=4326;POINT(144.933657 -38.3501913) | -38.3502 | 144.9337 | 2025-05-07 | 17 Charles Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Customer Leak |  |  | 20 |  | no | LD0012 |  | yes | 2hr travel 2hr onsite Arrived at property and meter was switched off. I knocked on property to inform the customer that I was carrying out leak detection, but no one was at the property. I turned on the meter so I could carry out the work. Probe down close to the back of the meter and had noise present but was just picking up the meter. The service then goes across the driveway and up to the property and then through the property, so there was expose pipe work going up the property, and that had very good noise on it. Went around the have of the property and there wad couple of outside taps to sound and I narrowed down the leak between the first two outside taps. I then had a look around the first tap, and I walked a bit further around and could hear a leak noise, and then I saw water running down bank. Please see the photos down below of location and leak, I have marked up the leak with a stick and sprayed it blue. I have isolated the supply again. | ec89740e-f694-4417-a78c-3513eabc4b82, 25c3ed69-7a1c-408d-823f-79b69f275799, 2ae74432-8453-4c30-8815-b17aa45be9ee, e568a757-31b7-4738-b904-e43517bc85ae, 908d5bf1-a6b5-4633-a86e-2e8278e6d083, a99e9d67-1a33-4cd7-973b-bbfe0bcab26f, 817d6e65-6123-4db3-9660-b24f3cac2cde |  | no
cdea7d43-d94a-479f-9dbd-075fbf2e9ee9 | 3 Somers Close McCrae Victoria 3938 Australia | 7 | 2025-04-30 00:35:23 UTC | 2025-05-13 23:42:01 UTC | 2025-04-30 00:22:45 UTC | South East Water | Stuart Haggett | Stuart Haggett | SRID=4326;POINT(144.93320366162249 -38.36070527066779) | -38.3607 | 144.9332 | 2025-04-30 | 3 Somers Close McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | investigation |  |  | 2 |  | no |  |  | yes | Noticed consistent flow of water across driveway 3, running across gravel road(Somers cl) & into gutter along Somers av Chased water to pvc pipe behind letterbox & lost sight of it. No noise on meter 3 Plan shows 2x valves after hydrant which I could not locate, suspect it has been buried/taken over by garden beds. One valve feeds dead end pvc main Sussopedly next to sewer manhole cover...could not locate & other valve heads downhill on Somers av Not sure Wether this is rainwater from recent rain, overflow water from watertank or leak on main somewhere. Suggest locating & exposing these 2 valves & sounding for leaks Difficulty locating meters along Somers cl. Could not locate some meters 14/5 Water still flowing. No rain for several days. Went to the very top to cook st to eliminate any possible customer leaks...found none.... ...although did notice that scour/overflow drain next to access driveway to watertank 90% full of water, but not flowing | c41afee0-9732-4d3e-8e93-f858602f3367, c0bb80ee-b327-4fd0-bb9a-54dfefd72406, 695a55bc-f36c-40e1-ad55-d15d2f74ec52, c6d8df06-c224-450f-8beb-a678cf137833, a03c737a-750f-4865-9b68-a9766c98082c, 2b3aa189-37bf-402f-adfc-b709e35a8481, dae9642c-ed09-40bc-8b7d-f7a968a022a1, 246cb3fe-67d2-4f64-839a-1b82d676b95e |  | yes
46c7646c-3070-4a99-90f5-e44bac4de709 | 75 Bayview Road McCrae Victoria 3938 Australia | 2 | 2025-05-12 21:41:38 UTC | 2025-05-13 23:09:21 UTC | 2025-05-12 21:38:09 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93577603466974 -38.35121330044794) | -38.3512 | 144.9358 | 2025-05-13 | 75 Bayview Road McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Meter |  |  | 0.3 |  | no |  |  | no | Leaking from meter connection?. Small noise on meter, meter pit full of water. Louder on service side Meter recently upgraded to digital meter | ca5e28a8-0bdc-44a8-8957-c8427d54b797, d903db96-15b4-401c-af77-f6e3c8a42ce1 |  | yes
3cc38b42-8daf-4229-92d1-366b2172e039 | 2 Bowen Street McCrae Victoria 3938 Australia | 3 | 2025-05-13 01:16:07 UTC | 2025-05-13 23:09:20 UTC | 2025-05-13 01:04:48 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.935884 -38.3517147) | -38.3517 | 144.9359 | 2025-05-13 | 2 Bowen Street McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Ferrule |  |  | 5 |  | no |  |  | no | Leak on ferrule Traced out service line which runs at angle & straightens out along naturestrip Probed onto main/ferrule which Is 1m deep & 1.4m behind gutter. Wet ground Small noise on meter Owner of 4 says there was a leak on ferrule 2 previously. Ferrule may have gone again. | adc1417b-c85e-4fb2-9b2e-c396c36107cf, b03f6e22-5dcf-40c2-875e-a1b2e15a06cf, 07f7f423-3a28-4db1-b872-50a210cd1da3 |  | yes
55d51c77-9ee1-42e0-b4cc-2176304fad35 | 80? Flinders Street McCrae Victoria 3938 Australia | 2 | 2025-05-13 04:24:15 UTC | 2025-05-13 23:09:19 UTC | 2025-05-13 04:20:02 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93100749512197 -38.357147452534704) | -38.3571 | 144.931 | 2025-05-13 | 80? Flinders Street McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Valve |  |  | 0.2 |  | no |  |  | no | Water in valve pit. Not sure if small leak on valve Picking up noise from prv station (wb131) No street number. Corner Flinders/Cairn | 9ece24a5-c80d-4bd1-8210-3960dd3dcb08, 08a61e42-67dc-49fb-9663-9d26c06b29a3 |  | yes
d090b9aa-0330-446c-9081-e273eaa6313a | 33 Wattle Place McCrae Victoria 3938 Australia | 5 | 2025-05-08 22:59:24 UTC | 2025-05-09 01:34:19 UTC | 2025-05-08 22:51:25 UTC | Service Stream | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.923299 -38.3527252) | -38.3527 | 144.9233 | 2025-05-09 | 33 Wattle Place McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Customer Leak |  |  | 5 |  | no | LD00011 |  | no | Arrived onsite, met with owner & he showed me where he thinks leak is In rear bungalow Can hear water hissing & wet patch next to front door/step/wall. Can also feel fine spray of water. Behind wall is laundry sink, sounded both taps (hot & cold) & cold tap is screaming. Confirmed that leak/burst is on cold tap line, somewhere behind wall. Looks like asbestos cement/wall panels Suggest they organise plumber to cut hole in wall to better pinpoint/find leak | f1b1e008-4bd9-4aa2-a7a0-746551d03880 |  | no
277fdd94-a688-4700-9d48-bf42b2ebd071 | 8 Bass Street McCrae Victoria 3938 Australia | 2 | 2025-04-29 03:48:13 UTC | 2025-04-29 23:12:51 UTC | 2025-04-29 03:43:16 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.9359505 -38.3572134) | -38.3572 | 144.936 | 2025-04-29 | 8 Bass Street McCrae Victoria 3938 Australia | McCrae | South East Water, Cook St Tank Zone | Stop Tap |  |  | 0.3 |  | no |  |  | yes | Found meter tap leaking again. Tightened meter tap, still leaking 0.1. Suggest replacing meter tap with gate valve meter tap. As this is the second time meter Tap has been leaking. | 4999ee4f-6a3c-4800-b1b2-c5ff09431001, 33f29b17-46db-4e0c-b5a5-84ef90fbc277 |  | yes
62206c5d-7230-4713-9f51-44fe57fd0b97 | 88 Cinerama Crescent McCrae Victoria 3938 Australia | 3 | 2025-04-16 00:39:38 UTC | 2025-04-16 02:10:42 UTC | 2025-04-16 00:35:14 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.9290052 -38.3630543) | -38.3631 | 144.929 | 2025-04-16 | 88 Cinerama Crescent McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Mains |  |  | 20 |  | no |  |  | yes | Corner Marina av. Next to agapanthus bushes & stormwater drain Water pushing through ground & running along naturestrip. Probed onto main, good noise, next to agapanthus bush Possibly on ferrule, couldn't locate meter 88 | 35222dff-8153-4205-a5e6-90bb5fe193ea, 604ec75f-6176-4e47-8734-924d9076894f, 75fea5f0-bd66-4645-9cf0-8cf14ac59b1d, 667a3dc7-4923-4c11-b9df-2a7ed13eb639, c3eef608-eb36-49a6-97c8-dec9ce765512 |  | yes
58f74c45-13f0-4225-9fb1-c3e069658d5e | 2 Grandview Court McCrae Victoria 3938 Australia | 2 | 2025-04-09 03:41:58 UTC | 2025-04-11 00:02:45 UTC | 2025-04-09 03:33:08 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.94330854874335 -38.35129796590364) | -38.3513 | 144.9433 | 2025-04-09 | 2 Grandview Court McCrae Victoria 3938 Australia | McCrae | South East Water, Cook St Tank Zone | Mains |  |  | 7 |  | no |  |  | yes | Possible leak on main, between driveway & sleeper wall. Ground soft , wet & boggy, couldn't probe onto main, unknown location Distant noise on hydrant Leak Possibly on T Junction of 100upvc & 63pe. May need to excavate/vacuum to locate main & chase water to leak Sewer runs Parralel to main | 1d976860-81a8-4660-a52e-e17b16fd509c, 990b7d15-85e6-43d1-bfc5-204d1d610d96, 945d7bfd-894f-45b8-b7bd-692450bc0aad, f1a54638-33b9-4e64-8bd7-b76fbd89ff26, 1b5b24a9-887a-47b4-97c4-7c0ed8877d30 |  | yes
be886058-ecc4-4be5-8ead-0ad2b70fb106 | 21 Charles Street McCrae Victoria 3938 Australia | 3 | 2025-04-03 03:41:18 UTC | 2025-04-03 22:15:54 UTC | 2025-04-03 03:20:32 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.9340256706488 -38.35028299700029) | -38.3503 | 144.934 | 2025-04-03 | 21 Charles Street McCrae Victoria 3938 Australia | McCrae | South East Water, Waller Place | Main to Meter Line |  |  | 2 |  | no |  |  | yes | Noticed sweat patch on road, sponged dry & water slowly weeping through Noticed previous tracer marks on road. Sounded along tracer marks & found noise. Leak on service line under road, approximately 1m from gutter | e8a8e81f-d51a-4108-8eca-304984f0923c, 7e2613fe-0972-420b-a949-e2a22de88a23, 2d6d82e6-601e-4130-9489-856546dbfbd8 |  | yes
a7d74ca5-98e4-48b8-8ee3-494f27b8f67c | 121 Bayview Road McCrae Victoria 3938 Australia | 2 | 2025-03-27 22:23:42 UTC | 2025-03-30 22:51:53 UTC | 2025-03-27 22:19:32 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93118715580397 -38.353960534298764) | -38.354 | 144.9312 | 2025-03-28 | 121 Bayview Road McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | possible leak |  |  | 3 |  | no |  |  | no | Good noise on meter, cannot access meter to confirm, sounds louder on service side . Noticed ground looks damp around meter & fence. Watering garden? Suggest gaining access to meter & shutting of meter to confirm if customer leak, service side leak or no leaks are present . | c5a844c4-e5e7-42c7-9ab9-d62868955bdf, 701c128a-211c-4f15-8e4c-8cc6f7283f51 |  | yes
9ef9b0a0-2c6e-4848-9318-775adb143531 | 26 Navigator Street McCrae Victoria 3938 Australia | 2 | 2025-03-27 23:51:20 UTC | 2025-03-30 22:51:52 UTC | 2025-03-27 23:49:40 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93581684541365 -38.35559490008938) | -38.3556 | 144.9358 | 2025-03-28 | 26 Navigator Street McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Hydrant |  |  | 8 |  | no |  |  | yes | Corner Matthew St. Ground hydrant leaking from ball | 6cb4a136-2c96-4391-92b2-3c167a641fd8, 875c0efe-c0b6-451f-a4cb-d2f5abc3a557 |  | yes
7af8ebcc-8440-4735-90e5-ef6549681887 | 30 Bowen Street McCrae Victoria 3938 Australia | 2 | 2025-03-28 01:08:18 UTC | 2025-03-30 22:51:51 UTC | 2025-03-28 01:06:31 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93773447412792 -38.35474643569958) | -38.3547 | 144.9377 | 2025-03-28 | 30 Bowen Street McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Hydrant |  |  | 2 |  | no |  |  | no | Ground hydrant leaking from ball | 97f9d53c-7f33-47ef-be9a-c4f5e400bd20, 5032a44c-cb7a-4699-8eba-d398e13da945 |  | yes
2186cd98-198e-41f9-862b-c7b22de8ec22 | 4 Outlook Road McCrae Victoria 3938 Australia | 2 | 2025-03-26 21:29:18 UTC | 2025-03-27 22:13:39 UTC | 2025-03-26 21:28:10 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.9420941 -38.3478989) | -38.3479 | 144.9421 | 2025-03-27 | 4 Outlook Road McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Meter |  |  | 0.4 |  | no |  |  | no | Leaking from both sides of meter connection | 86ea6205-b2b5-409f-a214-ad6d249ae49f, 4ec4459b-83ce-4878-883d-a2f20f9a429b |  | yes
5f433844-9953-483e-b816-6ef31e797255 | 12 Navigator Street McCrae Victoria 3938 Australia | 2 | 2025-03-27 20:50:53 UTC | 2025-03-27 22:13:36 UTC | 2025-03-27 20:47:42 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93387863053772 -38.35495697202377) | -38.355 | 144.9339 | 2025-03-28 | 12 Navigator Street McCrae Victoria 3938 Australia | McCrae | South East Water, Parkes St Tank Zone | Valve |  |  | 4 |  | no |  |  | no | Corner Flinders st. Valve leak. Water in pit | 159011c7-aba3-4d8e-9d10-9cc488500795, b27f1ee7-270f-4f6c-83ce-6da589fc2508, ece8f37c-805c-40b4-8310-1fe5e78d33d7 |  | yes
e5f07c10-99e9-4620-8269-cd084424bb10 | 37 Navigator Street McCrae Victoria 3938 Australia | 2 | 2025-03-24 23:01:10 UTC | 2025-03-26 00:09:42 UTC | 2025-03-24 22:59:39 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.93706874227433 -38.355787033467436) | -38.3558 | 144.9371 | 2025-03-25 | 37 Navigator Street McCrae Victoria 3938 Australia | McCrae | South East Water, Cook St Tank Zone | Stop Tap |  |  | 0.5 |  | no |  |  | no | Leaking from meter tap. Cannot tighten | af60ea14-07aa-4d9c-8641-8b8036413c2c, 63f94a2a-ce09-40ca-a9be-e833f7908d6d |  | yes
f6769554-937d-4bfb-a3c5-9f7d3e23fde4 | 8 Bass Street McCrae Victoria 3938 Australia | 3 | 2025-03-24 23:35:09 UTC | 2025-03-26 00:09:40 UTC | 2025-03-24 23:30:47 UTC | South East Water | Stuart Haggett | Luke Naylon | SRID=4326;POINT(144.9360668 -38.3571711) | -38.3572 | 144.9361 | 2025-03-25 | 8 Bass Street McCrae Victoria 3938 Australia | McCrae | South East Water, Cook St Tank Zone | Stop Tap |  |  | 5 |  | no |  |  | yes | Leaking from meter tap. Water shooting out everywhere. Cannot tighten. Owner knows of leak & has dug ditch next to meter. Water running down driveway & potentially affecting properties downhill Leak creating fair bit of noise, can be heard on surrounding assets | 5091ec76-decf-456e-9106-f3c65aa3a7f8, 31cd381f-39d8-4013-8735-c1147cd2fefd, 61dd67c2-3911-4606-89ff-20ad23ee00dd |  | yes
8860a7e5-7da3-44de-a4e2-599d23c16940 | 4 Waller Place McCrae Victoria 3938 Australia | 10 | 2025-01-15 23:03:10 UTC | 2025-02-11 04:01:33 UTC | 2025-01-15 02:41:57 UTC | South East Water | Morgan Williams | Scott Grace | SRID=4326;POINT(144.9377599489378 -38.34807677806307) | -38.3481 | 144.9378 | 2025-01-15 | 4 Waller Place McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | South East Water Report |  |  | 10 |  | no | NA |  | no | DS were originally requested by ServiceStream to attend water pushing up and flowing in the road at 4 Waller place on the 24/12/2024, at the time no leaks were detected, however a few concerns were raised with the amount of water gushing through storm water drains in the area. The new owners at 4 Waller and the owner Bret of number 5 (has lived here for the past 20 years) let us at the back of his block where he has an old Water style lid cover (see attached photos) it houses the 14” main elbow, it’s very deep approx 4m and is not on his property, although it’s fencing inside his property, we just popped the lid and sounded it directly, no noise at all. Apparently the drains run all year round, but the water has got a lot worse and it’s affected on the roadways and two locations bubbling up and damaging the road. On the 30/12/2024 we attended site again to survey uphill over the other side of the freeway, when we arrived on site SEW was in attendance and had detected a mains leak through bushland on the other side of the free way which I believe was repaired soon after and was not the cause of the issue at 4 Waller Place, as water was still flowing from the road. MW- 03/01/25 5hrs onsite Arrived onsite, and I started the investigation process fresh. I met Jason Marsh onsite, and he gave me a quick run down on what's been going on and what the issue is. Two leaks were located on this day, burst main outside of 29 Bayview Road and a fire hydrant leak outside of 115 Bayview Road. Burst main outside of 29 Bayview Road in my opinion was too small of a leak to be causing the issue at Waller Place and same with the fire hydrant leak. I did suggest having a vac truck onsite for the burst main to try and locate the main as it's PVC, I was unable to trace out the main and there's water breaking out on expensive driveway with water pooling out onside of naturestrip by the driveway, so vac truck would be suitable here because of the expensive driveway. Hydrant leak is an even smaller leak to this burst main, but it was still reported to Jason Marsh. After these two investigations were completed, I sounded around Waller Place where the original issue was and no leak noise was detected. I tested water myself with EC tester, and it had a reading of 600, which is nowhere near close enough to be mains water. I also noticed naturestrip around the side of Waller Place was soaking wet, which didn't make sense why water was breaking out down here. Back of property here was also really damp. MW- 06/01/25 6hrs onsite Had a phone call from Scott in the morning to say I needed back to Waller Place had a small avalanche happened near the job. I phoned Jason Marsh when I arrived onsite, and he suggested I start as fresh and suggested I should survey the area again. I sounded around Coburn Avenue/View Point Road and Prospect Hill Road, but it started to rain very heavily, and I was unable to listen in this weather, so I had to wait for the rain to stop but It was raining really heavily for most of the morning. After the rain calmed down, I resumed on what I was doing, but no major leak noise was detected. The avalanche happened on Penny Lane just below Viewpoint Road, so i re sounded that area again, but no leak noise was detected. MW- 08/01/25 8hrs onsite Arrived onsite and met Jason Marsh outside of the reservoir and assisted him in lifting large air valve cover. We lifted this and I sounded the air valve, and faint noise was picked up, but this air valve is directly outside of the reservoir and close to the pumping station so I believe i am just be picking up background noise from the pumps. Jason let me into the res and we both did an inspection around the res to see if we can spot any type of damp patch or something of concerned but nothing stuck out for us. Jason left to head back to sew office so he could print out a paper map for me so I could target areas to sound and actually have a plan to go off by. While he did this, I did carry on with the site and sounded downstream from where the water was breaking out from on Waller Place. Jason arrived back later with a plan and I carried on with the rest of the area for the day, I only came across couple of small noises to investigate but nothing of concern . MW- 09/01/25 8hrs onsite I carried on with surveying the plans provided , and I carried on sounding around Waller again and sounded further down on Burrell Street/Charles Street, etc, around this area today. A full scope of what I've done will be added further down on the report and highlighted. I picked up some noise but nothing major. There was background noise on Beverley road, but there is a prv here, which is causing the noise. I was unable to open the prv chamber up to inspect prv but listened on the valves on prv setup, and it's very loud here. I have noted noises down, and they will be checked later on. For the rest of the day, I just focused around these sections. MW- 10/01/25 4hrs onsite Just to note, I had half a day today as I booked annual leave off. Today I finished off downstream sections, I also sounded again near the res and noticed the main going off down a footpath so I walked that line to see if i could see any visible but nothing was detected. Just to note as well I double-checked plans again on the sew app as the paper plans were hard to work out, and there are two sections of mains coming off that PRV on customer properties. I have not walked these as I can't get access into these properties, but I would say if there was a leak on these sections, then these would be reported by the customers themselves. Next week, I will turn my attention to Bayview Road. MW- 14/01/25 8hrs Arrived onsite and I met Jason Marsh, where they repaired the previous burst main just on the other side of the freeway. He went through with me on what sections I should focus up here and said for me to sound Outlook Road, Arthur's Avenue, and the Boulevard and he also told me to run a correlation from the previous burst main up to the hydrant on Bayview Road where it tees off to and also the main runs down to the freeway onto the pumps. I was also asked to walk this section of main as well, but i was unable to due to the overgrown area and terrain. I sounded the areas in question, and no leak was detected. I was going to run a correlation today but decided to leave my enigmas out to a run an overnight correlation, which would be better as there would be less demand. I set these up to log area in question from 2am until 4am. I will pick these up tomorrow. Also, to note that another avalanche happened today in the same location as the last one. MW- 15/01/25 6hrs onsite Arrived onsite and picked up the loggers, I downloaded and at first glance it looked like they picked something up, but I was unable to input any measurements between the loggers as I could not physically measure out the distance myself so had to wait for Hayden from SEW to turn up so he can measure the distance out on his laptop. While I waited for Hayden, I carried on and completed my confirmations. I located a stop tap leak outside of 29 Coburn Avenue, but I repaired this myself and stopped the leak, but there was still slight noise on the meter. Quickly isolated, the supply and noise went indicating a possible internal leak. I quickly informed the customer to take a meter reading before heading off to bed just to confirm this. Located a possible burst main outside 22 William Street, which since I've been here has been reported as there was slight water showing. There is now a blue marker post here and I've sounded in naturestrip and u can pick up slight noise here but unable to locate meter for property so could be a service line leak but please see photos down below. Another small stop tap leak was picked up for 39 Beverley road which has been marked up. There was noise on Bartels street but it was just slight background noise on some assets in vicinity, its pvc here so I did run a quick correlation here but didn't get any luck but I can't see this to be causing the issue as its a good distance away. I met Hayden onsite around 12ish and he gave me measurements so I can run the correlations. As you can see in the photos down below, we are getting two different peaks, but I believe they are just picking up the noise from the pumps. The peak on logger 3 has pinned me directly in the pumping station ground, so I would ignore this and the other peak is around 6m from hydrant in bushland where they had the other Burst main. A suggestion here would be to have a vac truck onsite to expose the main as i can't probe down onto it to listen. But I think this is most likely picking up the pumps. In-conclusion I have completed my investigation and have informed Jason Marsh of the leaks I have detected. I don't believe any of the minor leaks detected are the cause of the issues at Waller Place or further downstream, I believe the issues are due to an underground stream. MW- 18/01/25 5hrs onsite I was requested by SEW to attend the site on Saturday to go over some of my work. I was first requested by Charles to sound Alexander Parade, which I did, and I didn't come across anything. After this, I then went back to waller Place and sounded main assets up there, but once again, no noise was detected. I decided to sound durry lane and hearn street as I didn't do these, but again, no noise was detected. MW- 20/01/25 4hrs onsite Arrived onsite and was informed by Jason Marsh that Burst main outside 29 Bayview road was attended by ServiceStream, and they used vac truck here but couldn't locate leak. I asked Jason for job notes from the crew, but he wasn't at his computer, and he didn't look at the photos himself. I called back here, and I ran a correlation here, but correlation didn't come up with anything. It's pvc here, so I didn't expect to get any results. Still water here and it's showing on driveway, I would need job notes from crew to see what they did but I would get a vac truck up here again and expose main on the otherside of the driveway as it's also wet here when probing, also suggest I'm onsite for this as well. After this, I waited for Jason to call to see what he wanted me to do, but he was busy himself on site. I was called away to check Sotto jobs close by. 04/02/25- 3hrs Started carrying out an extended survey, which was requested by SEW. Nothing major was located today, I had some conformations to go back on, but they weren't of great concern. 05/02/25- 3hrs Checked conformations from yesterday, and noises went indicating I was just picking up usage. Carried on surveying area for the rest of the day. Will be carrying on with the rest of the area tomorrow/Friday. 06/02/25- 8hrs Stuart Hagget made his way down to the site around mid-morning to assist me in surveying McCrae so we could finish it sooner. I made a plan with Stuart, and we split up the maps. I noticed on my maps that some of the sites I had already surveyed before, so there was no need for me to do these again. I had some more confirmations to confirm and will confirm these tomorrow. 07/02/25- 8hrs Myself and Stuart today carried on, and we finished the maps that we were given. For the rest of the day, we carried on with conformations. I located 3 leaks today, 2× leaking valves and a main to meter line leak. Only 1 valve leak is visible, but I estimate this to be doing around 0.7lpm. The other valve leak is in the vicinity of this, but water isn't showing, but it's very wet when probing down with FSB. The other leak i located was a main to meter line leak, but it's not a large leak and wouldn't be in connection with what is happening down in waller place. Stuart located a hydrant leak, which I believe I have already reported to SEW and a meter leak. These aren't large leaks at all. 10/02/25- 2hrs I had one more confirmation to confirm, but noise on meter went a lot quieter when listening today. I believe it was just usage/background noise I was picking up last time. | 7f3f4c9e-8e7f-4ae4-b389-ac8645c84371, 9d435bf5-9adf-44b1-a9db-940245f2658c, 50a9d470-b4af-43fc-86b1-3c19c605063d, 06eff4e3-7eff-40c2-b7df-93b17feb41a6, b25f8ef9-0783-43b2-bfb5-496aed0969bc, 582255f0-99b3-43ab-8e65-1204bbbc2866, ae86e788-3cce-450e-8c41-0451ed6dba42, b8eff733-469c-4a8a-9845-54608ecd4676, fe27ce96-1b09-4687-892a-0b46c9bd45ce, abab2fa9-52df-4452-b2a4-a1a07b456b88, d665ac16-a57c-4740-9e19-d75e94f2252c, 15a51de8-79d3-4d3a-a395-6e74f622e8f2, 43dd7957-f9c0-4fcd-9aac-53819fc80595, efd206f5-7ef8-4150-9ce3-e691cda485dc, 5cc2b328-d20c-4a4f-b774-991b19f90dd1, d733a25f-8412-489b-9472-4ba765b9dcbf, 210eac33-3530-4c69-82d3-89688a01f2f8, 5c534305-6ed0-4be2-b22a-c8ba716a20b4, 6f6fa079-fccf-47cc-a602-24146a2d0897, c35e4cd6-ef14-4a49-b387-edef7519bd14 |  | no
6f004a45-0783-40ad-8026-c65069ada9a0 | 69 Flinders Street McCrae Victoria 3938 Australia | 2 | 2025-02-06 23:32:52 UTC | 2025-02-08 01:47:41 UTC | 2025-02-06 23:30:16 UTC | South East Water | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.9321700541321 -38.356604504259174) | -38.3566 | 144.9322 | 2025-02-07 | 69 Flinders Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Meter |  |  | 0.5 |  | no | NA |  | no | Leaking on meter dial. Cracked screen. Water Spraying out | affb6a92-3aaf-4bd3-8725-3d27d29b5f1d, 085de8c5-db80-4bb8-83ec-c7660a299ce8 |  | no
73e6d484-16ea-4ad2-8991-34f8f8c1d28f | 115 Bayview Road McCrae Victoria 3938 Australia | 2 | 2025-02-07 00:36:40 UTC | 2025-02-08 01:47:40 UTC | 2025-02-07 00:35:20 UTC | South East Water | Stuart Haggett | Scott Grace | SRID=4326;POINT(144.93158700874324 -38.353800958867154) | -38.3538 | 144.9316 | 2025-02-07 | 115 Bayview Road McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Hydrant |  |  | 0.2 |  | no | NA |  | yes | Small leak on hydrant ball | c1b20271-a0ec-4f15-b6f1-95cecff426d8, 0a30e90a-dd93-4603-ab62-1bc2dbd05711 |  | no
2658bb2b-1077-48fb-9825-7253c2673380 | 8 Bowen Street McCrae Victoria 3938 Australia | 2 | 2025-02-07 01:21:19 UTC | 2025-02-08 01:47:40 UTC | 2025-02-07 01:18:42 UTC | South East Water | Morgan Williams | Scott Grace | SRID=4326;POINT(144.93605136774173 -38.352051859463835) | -38.3521 | 144.9361 | 2025-02-07 | 8 Bowen Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Valve |  |  | 0.7 |  | no | NA |  | yes | Leak located on Valve. Unable to get valve cover off, sounds like it could be packing. | 32a9be3b-5039-4c02-9101-52ef929f0339, e2b53689-b365-49fc-94a9-ba2d6d587b88, 9e2f6f5e-8508-4053-a5e8-e40a3029db16 |  | no
c3ad3557-98ff-43a3-bb82-48777444adb6 | 23 Flinders Street McCrae Victoria 3938 Australia | 2 | 2025-02-07 01:25:31 UTC | 2025-02-08 01:47:39 UTC | 2025-02-07 01:21:33 UTC | South East Water | Morgan Williams | Scott Grace | SRID=4326;POINT(144.93624745326318 -38.352429571322546) | -38.3524 | 144.9362 | 2025-02-07 | 23 Flinders Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Valve |  |  | 0.5 |  | no | NA |  | no | Suspected leak on valve. Picking up noise on valve and hydrant next to it hasn't got much noise on it. Managed to get the valve cover off, and there's no leak showing, but it's very saturated/wet in valve chamber when probing with FSB. | f0a68a83-28f3-44b7-a817-98f12771cb4c, c308a150-a8b4-4bc2-aa0c-3c88a8201115, 0f2531fb-3bd3-48a5-b18a-e4e25ee2532d |  | no
80b90180-2676-45a6-b177-cf3ee0695222 | 30 Somers Avenue McCrae Victoria 3938 Australia | 4 | 2025-02-03 23:01:33 UTC | 2025-02-04 01:07:25 UTC | 2025-02-03 22:41:37 UTC | Service Stream | Morgan Williams | Scott Grace | SRID=4326;POINT(144.9321631564614 -38.36014006406253) | -38.3601 | 144.9322 | 2025-02-04 | 30 Somers Avenue McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Ferrule |  |  | 2 |  | no | 1316822/001 |  | no | 03/02/25- 4hrs Arrived onsite and checked assets near 30 Somers Avenue, and no leak noise was detected. Checked 30 Somers Avenue, and the issue is still occurring. Read the job report, and water is making its way down from the NBN pits uphill. Chased the water around 9- 18 Somers Avenue. Water trickling in the pit outside of number 18, and it's also water holding in the pit outside number 9, which is directly opposite number 18. Pumped the water, which is holding, which is outside number 9, and I then checked the Pit opposite where water was trickling in, and that stopped indicating they arr linked together. There is noise on number 9 service as well as number 18, but they both sound the same. Deployed enigmas overnight and will will cheek the results tomorrow. 04/02/25- 2hrs Returned to site and checked the results from yesterday, and it gave me a peak 25m from the hydrant in naturestrip, which is near number 9. Frequency levels here aren't best, but it was a long correlation I did, and also it being AC here didn't help as well. Measured out the peak, and it's peak me near enough on number 9 service/ferrule. Sounded service again, and I quickly isolated the supply and noise stays on the meter. This is also about 0.5m from the telstra pit as well. Main has been marked up in the roadway, but my plans are showing it to be in naturestrip as that's where also the assets are located and they are showing to be dircet on the plans as well. Unable to trace out the main due to it being AC. Tried to listen for surface noise but was unable to pick up any noise. Suggestions here would be exposed and excavate my markup location and expose the ferrule as well for number 9 to try and capture leak. | 7a6aed0a-41fc-4806-9a02-26bbe8b0e245, 757acd48-ee28-4a1c-9df2-d360c6a58561, ab834083-5e94-44fe-8ab8-a48d8087fce3, 5d846f71-958d-4b92-8c51-90417216d064 |  | no
f4cfc083-b54c-46b6-94b1-4d0a4cf006d4 | 22 William Street McCrae Victoria 3938 Australia | 2 | 2025-01-17 00:27:57 UTC | 2025-01-17 00:51:52 UTC | 2025-01-17 00:11:41 UTC | Downer | Morgan Williams | Scott Grace | SRID=4326;POINT(144.9302495 -38.3525179) | -38.3525 | 144.9302 | 2025-01-17 | 22 William Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Mains |  |  | 0.3 |  | no | 1301391/001 |  | yes | Suspect there's a small leak on the main here. I have ran a quick correlation here, but correlation didn't bring up anything, but there's not much noise here. There's only a very slight noise on the Fire plug further up. I have probed down in naturestrip, but I'm unable to get onto the main to listen directly as it's 80mm AC here, so im probably just missing the main. I did listen anyway, and I think I might be picking up the faintest of noise, but it's hard to tell. This is directly in line with the main and its seeping down driveway now, and the customer is concerned due to the incident down Penny Lane. I think it's just a very small leak on the main here, and I'm just unable to hear it. I'm unable to test the water myself. Suggest excavating around wet patch to expose main. MW 1.5hr travel & 1.5hr onsite | 8e18cddb-1dd8-4824-a623-1b7354f4dc8e, b2a58132-9ffa-4712-b367-a0dfd0458d5e, e539a2bd-5034-4686-8de8-e3d9df59d18c |  | no
a4c184c5-834f-4d6e-8fcb-cde7b68b94a0 | 4 Waller Place McCrae Victoria 3938 Australia | 8 | 2024-12-24 02:23:20 UTC | 2025-01-15 02:05:32 UTC | 2024-12-23 23:34:19 UTC | Service Stream | Simon Gabriel | Morgan Williams | SRID=4326;POINT(144.9380914 -38.3479905) | -38.348 | 144.9381 | 2024-12-24 | 4 Waller Place McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Mains |  |  | 120 |  | yes | 1295094/003 |  | no | 30/12/2024 GS Attended site at the request of Jason to extend our investigation on the otherwise of the free way, SEW had already been onsite earlier in the morning and discovered a mains leak on the other side of the freeway. 24/12/24 Simon from DS and Jason Marsh (SEW) on-site to investigate Sounded all assets in the area, followed suspect 300mm main and no leaks were detected. Chlorine sample needs to be taken when rain stops. The new owners at 4 Waller and the owner Bret of number 5 (has lived here for the past 20 years) has let us at the back of his block where he has an old Water style lid cover (see attached photos) it houses the 14” main elbow it’s very deep 4m is actually not on his property, although it’s fencing inside his property, we just popped the and sounded it directly, no noise at all. Apparently the drains run all year round, but the water has got a lot worse and it’s affected on the roadways and two locations bubbling up and damaging the road. It been partially barricaded of. We also surveyed Bayview Rd above the Highway with no leak noises detected. I don’t believe there’s any leaks on the mains but still some of the smaller pipes really haven’t checked out. Jason Marsh will return take samples when it’s not raining for a few days. | 829242f7-e56a-4f40-9548-fcfced064c60, cb2e4bf3-1ec0-41e2-97d8-4f58c9a74833, 31af4a23-9de8-4712-a4f0-0623ac1337bc, a8d431c6-8dd9-4747-aa44-a7e1d3579d93, 6612b5fb-da58-4703-b0ac-869f178dd4ea, 561f1314-5da3-458c-9434-3bfd541be460, 1c431b5b-c5f1-4937-a90e-d9341a59cdbc, cee054a9-7e98-481a-a136-988c5a9cd9e9, fd88c562-a5b5-481f-9805-1ded32676668, 5de28830-d3cc-499c-bc0b-6eae11c3ee96, a3b3df70-f12c-46eb-80af-2f55efa0365a, f6480d0c-c418-4cd9-a4ea-a7ef4d1b2357, 87dd5320-cde1-4678-b64b-eeac88250677, 2160f841-900d-4209-970e-d56c16b9e0e8, 93456a90-4f6c-419c-98d7-a7034027d367, b2ebf945-4b94-4398-8e52-e3822814effc, b76c70eb-aabf-40e1-9ea7-9aeb153a23bb, e26747b3-a109-4929-9ccb-ec94073be7ba, b57dab8d-c3ef-4999-83a5-44db178502d0, 152c4d11-8163-4fe4-b13b-65dab0f96580, badd9a6b-3105-4d74-bd58-4a0fea996f88, b5c54e3a-ea78-453e-97ef-6ecc7298f22c |  | no
756810a7-ec2e-4246-9358-d35f4b731c65 | 9 Catherine Street McCrae Victoria 3938 Australia | 4 | 2024-11-12 00:47:38 UTC | 2024-11-12 23:53:16 UTC | 2024-11-11 23:53:08 UTC | Service Stream | Stuart Haggett | Stuart Haggett | SRID=4326;POINT(144.92821453498985 -38.351663080146935) | -38.3517 | 144.9282 | 2024-11-12 | 9 Catherine Street McCrae Victoria 3938 Australia | McCrae | South East Water, Reactive Leaks | Mains |  |  | 7 |  | no | 1276376/1 |  | no | 12/11 Sounds like leak is on main. Bailed out stormwater pit 5A & it's filling up from agi pipe Slight noise on surrounding assets. No access to meter 5a. Probed onto ferrule 5A, very good noise, bone dry though. Probed numerous holes along 80ac main, getting good noise, but bone dry ground. Sounds louder toward ferrule 5A. Suggest DS be onsite with dig crew, exposing above & below ferrule 5a, shutting off ferrule 5a to confirm if leak on service line, customer side or on main. If no result suggest correlating directly from ferrule to hydrant on corner or hydrant uphill 30min travel 2hr onsite 13/11 Onsite with dig crew Exposed ferrule, Correlation peaked on ferrule, tiny leak on tapping connection....may have been knocked whilst excavating, Replaced tapping, still leaking, found tiny leak on ferrule , replaced ferrule Recharged main, still leak noise present . Ran another correlation, still peaking on ferrule. Probed a few more holes, loudest hole approximately 1m away from ferrule Dug down, discovered buried telstra pit & found leak directly below telstra pit, pinhole leak on 80ac main 1hr travel 3.5 hr onsite | ebfe92f3-0f1d-4b8a-b456-fcf2a5660a88, dc8ec2eb-e3ba-4293-ae83-d9fb7acce52a, b266c8e5-9c1c-412e-bad1-f2bc3a874e94, d64cdfb2-3aa5-474d-9550-f54cab2df162, 10d42fc6-e611-45fc-aa55-b30697799102, 73a7c243-8489-4be7-8794-a18072bbfda1, 61136f99-c39c-4de8-88f7-3105fb261738, 4cbb12b4-c4c4-461b-9fd9-cc2e1ae2fad7, e33beab8-a707-4e95-bb11-93052c1db0ec, 30ae8d88-ca2e-4b53-8f52-5382b06335c2 |  | no